## Equipment Schedule
LEGACY BUSINESS ENGINEERS LTD
MECHANICAL EQUIPMENT SCHEDULE
Project: [NAME] ¦ Rev: [A] ¦ Date: [DD/MM/YYYY]
Ref | System | Equipment Type | Duty/Capacity | Unit | Qty | Redundancy | Location | Floor | Plant Room/Zone | Equipment Dims L×W×H (mm) | Weight (kg) | Maintenance Clearance (mm) [Source] | Total Zone incl. Clearance L×W×H (mm) | Access Requirements | Connection Sizes (Flow/Return) | Electrical Supply | kW Input | Control Interface | Noise dB(A) | Refrigerant/Medium | Design Standard | Notes
HEATING
H-01 | Heating | Gas Boiler / ASHP |  | kW |  | N+0 or N+1 | [5 empty] | 1000 front, 600 sides [BSRIA BG 20 Table 3.1] |  |  | DN50 F/R LTHW | 400V 3ph |  | BMS |  |  | IS EN 15502 / EN 14511
H-02 | Heating | LTHW Pump Set |  | l/s @ kPa | 2 | Duty/Standby | [5 empty] | 600 all sides [BSRIA BG 20 §3.2] |  |  | DN32 F/R | 400V 3ph |  | BMS |  | Water | Europump / ErP
H-03 | Heating | Expansion Vessel |  | litres | 1 | N+0 | [5 empty] | 300 all sides [Manufacturer IOM] |  |  | DN20 | N/A |  | N/A |  | N/A | BS 7074-1 / EN 13831
COOLING
C-01 | Cooling | Chiller / VRF Outdoor |  | kW |  | Per mfr | External |  |  |  |  | 1500 front, 1000 sides [EN 14511 / Mfr IOM] |  | Crane access | Ref piping per mfr | 400V 3ph |  | BMS |  |  | EN 14511 / EN 14825
C-02 | Cooling | CHW Pump Set |  | l/s @ kPa | 2 | Duty/Standby | [5 empty] | 600 all sides [BSRIA BG 20 §3.2] |  |  | DN40 F/R | 400V 3ph |  | BMS |  | Water | Europump / ErP
C-03 | Cooling | FCU / VRF Indoor |  | kW |  | N+0 | Ceiling void |  |  |  |  | 450mm below [BSRIA BG 20 Table 3.3] |  | Access panel min 600×600 | DN15 F/R | 230V 1ph |  | Local+BMS |  |  | EN 1397
VENTILATION
V-01 | Ventilation | AHU (Supply+Extract) |  | m³/s |  | N+0 | [5 empty] | 1200 filter, 800 others [BSRIA BG 20 Table 3.2] |  | Full panel removal | Duct spigots per schedule | 400V 3ph |  | BMS |  | Air | EN 13053 / ErP
V-02 | Ventilation | Extract Fan |  | l/s @ Pa |  | N+0 or N+1 | [5 empty] | 600 all sides [BSRIA BG 20] |  |  | Duct spigot | 400V 3ph |  | BMS |  | Air | BS 848 / ErP
DHW & PLUMBING
P-01 | Plumbing | Calorifier |  | kW / litres |  | N+0 | [5 empty] | 600 front, 300 sides [BSRIA BG 20 Table 3.4] |  |  | DN25 CW, DN25 HW, DN20 sec return | 400V 3ph |  | BMS |  | Water | BS 853 / CIBSE Guide G
P-02 | Plumbing | CW Storage Tank |  | litres |  | N+0 | [5 empty] | 600 all sides [BS 8558 §6.3] |  | Structural check | DN32 inlet, DN40 outlet | N/A |  | BMS level |  | Water | BS 8558 / WRAS
FIRE PROTECTION
F-01 | Fire | Sprinkler Pump Set |  | l/min @ bar |  | Duty/Jockey | [5 empty] | 1000 front, 600 sides [BS EN 12845 §10.4] |  |  | DN100 suction, DN80 delivery | 400V 3ph |  | Fire panel |  | Water | BS EN 12845 / IS 3218
NOTES:
1. Delete unused system sections before issue. Blank rows with system names may be read as "included but not sized."
2. Maintenance clearance: BSRIA BG 20 (2023) unless stated. Verify against manufacturer IOM.
3. Total Zone = Equipment dims + clearance on all sides. Provide to architect for room sizing.
4. Connection sizes indicative at scheme design — confirm from hydraulic calcs at detailed design.
5. Redundancy: N+0 = no standby, N+1 = one standby, Duty/Standby = two units each at full load.